## Monthly Checklist
LifeSafetyWiki [Your Organization]
MONTHLY FIRE PUMP RUN CHECKLIST
No-flow/churn run checklist for inspection, testing, observation, documentation, and follow-up.
FACILITY | FACILITY | FACILITY | TEST DETAILS | TEST DETAILS | TEST DETAILS | PUMP / DRIVER | PUMP / DRIVER
Organization | [Your Organization] | [Your Organization] | Year | 2026 | 2026 | Pump ID
Facility / Campus |  |  | Month |  |  | Driver Type | Electric
Pump Location |  |  | Date Tested |  |  | Start Method | Pressure Drop / Controller Test
Rated GPM / PSI |  |  | Start / End Time |  |  | Tester
Monitoring / Panel | [5 empty] | Actual Duration
Healthcare basis: TJC PE.04.01.01 EP 2 ¦ NFPA 25 Ch. 8 ¦ NFPA 101-2012 §9.7.5 ¦ CMS K353 ¦ Confirm adopted edition/AHJ requirements.
P = Pass / no issue ¦ C = Problem identified & corrected ¦ F = Fail / management notified ¦ N/A = Not applicable
TOTAL ITEMS | TOTAL ITEMS | ENTERED | ENTERED | PASSED | PASSED | FAILED | FAILED
29 |  | 0 |  | 0 |  | 0
CORRECTED | CORRECTED | N/A | N/A | COMPLETION | COMPLETION | OVERALL RESULT | OVERALL RESULT
0 |  | 0 |  | 0% |  | NOT STARTED
INSPECTION / TESTING CHECKLIST
Section | # | Checklist Item | Record / Verify | Status | Initials | Notes / WO / LSRA / ILSM | Field Trigger
Pre-Run | 1 | Notify monitoring point / command center as required. | System placed on test only where required by facility procedure; occupants/vendors notified as needed. |  |  |  | Facility procedure
Pre-Run | 2 | Pump room accessible and acceptable. | Access clear, lighting working, no storage blocking pump/controller/valves, room temperature acceptable. |  |  |  | NFPA 25 / housekeeping
Pre-Run | 3 | No active impairment before test. | Document existing alarms, troubles, leaks, valve closures, low heat, or controller concerns before starting. |  |  |  | Impairment check
Pre-Run | 4 | Suction/discharge valves open and supervised. | Do not operate valves unless authorized; verify valves are open, locked/sealed/supervised where applicable. |  |  |  | NFPA 25 Ch. 8
Pre-Run | 5 | Controller normal and in automatic. | Power available; no controller trouble; power light/normal indicator observed. |  |  |  | NFPA 25 Ch. 8
Pre-Run | 6 | Jockey pump status checked. | Jockey pump available; pressure maintained; no abnormal cycling noted. |  |  |  | System pressure
Pre-Run | 7 | Record starting pressures. | Suction PSI: ____ Discharge PSI: ____ System/Jockey PSI: ____ |  |  |  | Record readings
Pre-Run | 8 | Packing gland / mechanical seal checked before run. | Slight packing leakage may be normal; dry packing, excessive stream, or seal leakage gets a note. |  |  |  | Pump condition
Start | 9 | Pump started by acceptable method. | Prefer automatic start by pressure drop/test arrangement unless facility procedure/manufacturer/AHJ directs otherwise. |  |  |  | Start method
Start | 10 | Pump starts and accelerates smoothly. | Record start pressure and any delayed start, hard start, breaker/controller issue, or abnormal sound. |  |  |  | Start observation
Run | 11 | Full run duration completed. | Electric: 10 minutes where permitted; Diesel: typically weekly 30 minutes. Verify adopted edition and pump configuration. |  |  |  | NFPA 25 Ch. 8
Run | 12 | Fresh suction/discharge readings recorded. | Start/Mid/End: Suction PSI ___ / ___ / ___; Discharge PSI ___ / ___ / ___. Do not carry forward readings. |  |  |  | Record readings
Run | 13 | Relief/circulation valve operation observed. | Relief/circulation discharge observed as expected; no overpressure or abnormal discharge condition. |  |  |  | Overheat prevention
Run | 14 | Packing gland condition observed during run. | Slight drip correct for packing; dry, hot, excessive, or streaming leakage requires follow-up. |  |  |  | Pump condition
Run | 15 | Bearing, casing, packing box, and coupling checked for heat. | No abnormal heat. Hot-to-touch or unusual temperature rise requires note/escalation. |  |  |  | Alignment warning
Run | 16 | Listen/feel for unusual noise or vibration. | Bearing growl, buzzing coupling, shaft wobble, rubbing, grinding, or new vibration compared to prior runs gets a note. |  |  |  | Alignment warning
Run | 17 | Electric driver / motor condition observed. | No abnormal vibration, heat, odor, smoke, electrical issue, or coupling guard concern. |  |  |  | Driver condition
Run | 18 | Controller indicators and power condition verified. | Power light/normal indicator, pump running indication, no phase reversal/power trouble where monitored. |  |  |  | Power / controller
Run | 19 | Valves, switches, and piping checked. | No leaks, loose components, damaged switch, closed valve condition, or obstruction around pump assembly. |  |  |  | NFPA 25 Ch. 8
Run | 20 | Overheating risk checked during churn/no-flow. | No abnormal casing/bearing/packing-box heat; circulation/relief functioning; no recirculation overheating concern. |  |  |  | No-flow risk
Shutdown / Restore | 21 | Pump shut down per proper procedure. | Pump stopped normally; no restart cycling or trouble after shutdown. |  |  |  | Restore
Shutdown / Restore | 22 | Controller restored to AUTO/normal. | Controller left in AUTO; normal indicators verified; no lockout/manual/off condition left behind. |  |  |  | Restore
Shutdown / Restore | 23 | Jockey pump restored/normal. | Jockey pump returned to normal operation; system pressure stabilized. |  |  |  | Restore
Shutdown / Restore | 24 | Alarms/supervisory/monitoring restored. | Monitoring point notified test is complete; panel/monitoring system normal or remaining troubles documented. |  |  |  | Restore
Shutdown / Restore | 25 | Final pressures recorded. | Final suction PSI: ____ Final discharge/system PSI: ____ |  |  |  | Final readings
Documentation | 26 | Deficiencies documented with corrective path. | If C or F is used, explain issue, correction, vendor/work order, manager notification, and follow-up date. |  |  |  | Documentation
Documentation | 27 | Management notified for F items/incomplete run. | Notify management when run cannot be completed or a condition may affect pump reliability. |  |  |  | Escalation
Documentation | 28 | Impairment, LSRA, and ILSM considered if applicable. | Use facility policy for impaired fire protection, incomplete test, unrepaired deficiency, or reduced reliability. |  |  |  | LSRA / ILSM
Documentation | 29 | Permanent pump record updated. | File monthly checklist, work orders, vendor notes, annual flow curve, lubrication, alignment, and repair records. |  |  |  | Records
NOTES & FOLLOW-UP ACTIONS
EXAMPLE F NOTE — ABNORMAL HEAT / VIBRATION AT COUPLING OR ALIGNMENT SHAFT
Full 10-minute run test was not completed due to abnormal heat and vibration observed at the coupling/alignment shaft between the electric motor driver and fire pump. Management notified. Refer to Manager’s Notes, LSRA, and ILSM documentation for corrective action and follow-up.
Inspection/testing performed in accordance with facility policy and applicable adopted standards. Confirm latest editions with your organization, AHJ, CMS/state requirements, and manufacturer instructions.

## Yearly Log
LifeSafetyWiki — Fire Pump Monthly Run Yearly Log
Use one row per monthly test. Status fields use the same P / C / F / N/A dropdown logic as the monthly checklist.
Month | Date | Tester | Driver | Start PSI | Suction PSI | Discharge PSI | Relief/Circ Valve | Packing Gland | Jockey Pump | Run Duration | Noise / Vibration | Overheat Check | Overall Result | Notes / Corrective Action
January
February
March
April
May
June
July
August
September
October
November
December
Footer: Per TJC PE.04.01.01 EP 2 ¦ NFPA 25 Ch. 8 ¦ NFPA 101-2012 §9.7.5 ¦ CMS K353 ¦ Confirm adopted edition/AHJ requirements

## References
LifeSafetyWiki Fire Pump Checklist — Reference Notes
Type | Reference | How it connects to this checklist | Source / URL
LifeSafetyWiki article | Fire Pump Testing & Alignment | Checklist emphasizes heat, vibration, coupling/alignment area, pressure readings, and observation during the churn/no-flow run. | https://www.lifesafetywiki.com/wiki/fire-pump-testing-and-alignment
Inspection/Testing/Maintenance | NFPA 25, Chapter 8 | Primary ITM standard for ongoing fire pump inspection, testing, maintenance, no-flow/churn observations, and records. | Confirm adopted edition for your facility/AHJ.
Healthcare Life Safety | NFPA 101-2012 §9.7.5 | Healthcare fire protection systems are maintained and tested through referenced standards such as NFPA 25. | Confirm adopted edition and CMS/state adoption.
CMS Survey Tag | CMS K353 | Survey basis for sprinkler/standpipe ITM and recordkeeping; commonly connects healthcare facilities back to NFPA 25. | https://www.cms.gov/Medicare/CMS-Forms/CMS-Forms/downloads/cms2786R.pdf
Accreditation | TJC PE.04.01.01 EP 2 | Supports maintaining fire/life-safety systems and essential equipment in safe operating condition. | Confirm current TJC manual/program applicability.
Installation/Acceptance | NFPA 20 | Installation/acceptance standard for stationary fire pumps; useful when alignment, coupling, controller, or installation-related concerns are found. | Confirm adopted edition and manufacturer instructions.
Electrical Safety | NFPA 70E | Useful for electrical hazard awareness around pump controllers, power, phase reversal, and troubleshooting; not a substitute for qualified electrical work. | Confirm facility electrical safety program.
Local Authority | AHJ / State of Georgia / CMS | State, local fire marshal/AHJ, and CMS adoption can control the applicable editions and enforcement expectations. | Confirm with your organization and AHJ.
Note: Confirm the latest applicable standards, editions, adopted codes, AHJ direction, and state requirements before using this form as an official compliance record.

## Lists
Status | Years | Months | Driver Type | Start Method
P | 2024 | January | Electric | Pressure Drop / Controller Test
C | 2025 | February | Diesel | Manual Controller Start
F | 2026 | March | Electric + Diesel | Automatic Start by System Demand
N/A | 2027 | April |  | Other / AHJ Approved
| 2028 | May |  | Not Tested
| 2029 | June
| 2030 | July
| 2031 | August
| 2032 | September
| 2033 | October
| 2034 | November
| 2035 | December