## Read me first
TJC Survey Readiness Toolkit
LifeSafetyWiki by Samektra ¦ lifesafetywiki.com/wiki/joint-commission-survey-binders
What this is | Five working sheets that turn a pile of inspection reports into a retrieval system. Fill them in once, keep them current, and you can answer any Life Safety Code Surveyor document request in about a minute.
Who it is for | Hospitals and critical access hospitals accredited by The Joint Commission. Much of it also works for CMS Life Safety Code surveys and state fire marshal inspections, because the underlying records are the same.
Sheet 1 - Binder Index | The 'where to find it' sheet. Put a printed copy in the front of Binder 0 and give one to the surveyor at the opening conference.
Sheet 2 - Inspection Matrix | Every ITM record TJC's document tool asks for, with its code citation and frequency. Fill in Last Completed / Next Due / Binder / Tab. This is the sheet that answers 'show me your annual fire alarm inspection.'
Sheet 3 - Deficiency to Closure | The lifecycle tracker. A deficiency is not closed when it is repaired; it is closed when the repair is verified and the evidence is filed. This sheet is the proof.
Sheet 4 - Fire Drill Matrix | Five quarters, every shift. TJC's document tool asks for five quarters of fire drill data, not four.
Sheet 5 - Survey Day Request Log | Fill this in live during the survey. It tells you what you were slow on, which is next year's homework.
Sheet 6 - Binder Spines | Print, cut, slide into the spine pockets. Set your printer to Actual Size, not Fit to Page.
Where the citations come from | The Inspection Matrix rows, frequencies and NFPA references are transcribed from The Joint Commission's Hospital Life Safety & Environment of Care Document List and Review Tool (effective 3/1/2024). Nothing here is invented. Confirm against the current edition on the TJC Physical Environment portal before you rely on it.
The 2026 change | Effective January 1, 2026 the Environment of Care (EC) and Life Safety (LS) chapters were consolidated into a single Physical Environment (PE) chapter, and the Survey Process Guide (SPG) replaced the Survey Activity Guide. The records did not change. The chapter labels did. Old standard numbers on your tabs are not a finding as long as the underlying requirement is still met.
Not legal or code advice | This is a documentation organizing aid produced by Samektra, an independent safety consultancy. It is not published, endorsed or reviewed by The Joint Commission, CMS or NFPA. Your accreditation manual, the current SPG and your Authority Having Jurisdiction govern.

## 1 Binder Index
Master Binder Index
Hand a printed copy to the surveyor at the opening conference. This is the map.
Binder | Contents | Tabs | Owner | Location (physical) | Electronic path
0 - Survey Command | Index, building information, Life Safety drawings, building assessment, SOC / BBI, AHJ documents, approved equivalencies and waivers, open deficiency summary, ILSM summary, inspection calendar | 0.1 - 0.12
1 - Fire Alarm | Annual fire alarm inspection and test, initiating devices, notification appliances, duct detectors, supervisory devices, monitoring and transmission, door release, HVAC shutdown interface | 1.1 - 1.8
2 - Suppression | Sprinkler quarterly and annual ITM, waterflow, tampers, main drains, fire pump weekly / monthly / annual, FDC, standpipe, dry and preaction, kitchen suppression, clean agent and CO2 | 2.1 - 2.11
3 - Barriers & Doors | Annual fire door inspection, rolling and sliding doors, dampers, barrier surveys, above-ceiling findings, penetration repairs, door deficiency tracking, reinspection evidence | 3.1 - 3.8
4 - Emergency Power | Weekly EPSS inspection, monthly generator load test, ATS testing, monthly egress lighting, annual 90-minute battery test, fuel quality, SEPSS, 36-month load test | 4.1 - 4.8
5 - Medical Gas & Utilities | Medical gas inventory and certification, source equipment, alarms, zone valves, vacuum, utility system inventory and risk assessment, water management program | 5.1 - 5.7
6 - Fire Drills | Five quarters of drills, every shift, every building. Each drill: record, staff participation, alarm transmission, critique, corrective action | 6.Q1 - 6.Q5
7 - LSRA / ILSM / Construction | Life safety risk assessments, ILSM policy, ILSM assessments and implementation logs, fire watch records, impairments, construction projects, temporary barriers, above-ceiling permits, ILSM termination | 7.1 - 7.9
8 - Deficiency & Corrective Action | Master deficiency register, work orders, risk assessments, interim measures, completion evidence, verification sign-off | 8.1 - 8.6

## 2 Inspection Matrix
Inspection Frequency Matrix
Rows, frequencies and code references transcribed from TJC's Hospital LS & EC Document List and Review Tool (effective 3/1/2024). Verify against the current edition.
Document / Requirement | Code reference | Frequency | Last completed | Next due | Binder | Tab | Owner | Deficiencies? | Evidence on file?
Pressure supervisory indicating devices (high- and low-air pressure switches), water level, water temperature, room temperature and other suppression supervisory initiating devices | NFPA 72-2010 Table 14.4.5 | Quarterly
Valve supervisory switches | NFPA 72-2010 Table 14.4.5 | Semiannual
Other supervisory initiating devices | NFPA 72-2010 Table 14.4.5 | Annually
Water flow devices | NFPA 72-2010 Table 14.4.5; NFPA 25-2011 Table 5.1.1.2 | Semiannual
Tamper switches | NFPA 72-2010 Table 14.4.5 | Semiannual
Duct, heat and smoke detectors, and manual fire alarm boxes | NFPA 72-2010 Table 14.4.5; 17.14 | Annually
Notification devices (audible and visual) and door-releasing devices | NFPA 72-2010 Table 14.4.5 | Annually
Emergency services notification transmission equipment | NFPA 72-2010 Table 14.4.5 | Annually
Electric motor-driven fire pumps tested under no-flow conditions | NFPA 25-2011 8.3.1; 8.3.2 | Monthly
Diesel-engine-driven fire pumps tested under no-flow conditions | NFPA 25-2011 8.3.1; 8.3.2 | Weekly
Sprinkler system main drain tests on all risers | NFPA 25-2011 13.2.5; 13.3.3.4; Table 13.1.1.2; Table 13.8.1 | Annually
Fire department connections inspected | NFPA 25-2011 13.7; Table 13.1.1.2 | Quarterly
Fire pump(s) tested under flow; supervisory signals for pump running and pump power loss tested | NFPA 25-2011 8.3.3; 8.3.3.4 | Annually
Standpipe flow test | NFPA 25-2011 6.3.1; 6.3.2; Table 6.1.1.2 | Every 5 years
Kitchen suppression system testing | NFPA 96-2011 11.2 | Semiannual
Carbon dioxide systems tested | NFPA 12-2011 4.8.3.2 | Annually
Smoke detection shutdown devices for HVAC tested | NFPA 90A-2012 6.4.1 | Annually
All horizontal and vertical roller and slider doors tested | NFPA 80-2010 5.2.14.3; NFPA 105-2010 5.2.1; 5.2.2 | Annually
Inspection and testing of fire door assemblies by a qualified person (excludes nonrated doors, including corridor doors to patient care rooms and smoke barrier doors) | NFPA 101-2012 7.2.1.5.10.1; 7.2.1.5.11; 7.2.1.15; NFPA 80-2010 4.8.4; 5.2.1; 5.2.3; 5.2.4; 5.2.6; 5.2.7; 6.3.1.7; NFPA 105-2010 5.2.1 | Annually
Elevators with firefighters' emergency operations | NFPA 101-2012 9.4.3; 9.4.6 | Monthly
Functional test of emergency lighting and exit signs required for egress and task lighting, minimum 30 seconds, plus visual inspection of other exit signs | NFPA 101-2012 7.9.3; 7.10.9; NFPA 99-2012 6.3.2.2.11.5 | Monthly
Functional test of battery-powered lights on the egress and exit sign inventory, 1 1/2 hours | NFPA 101-2012 7.9.3; 7.10.9; NFPA 99-2012 6.3.2.2.11.5 | Annually
Functional test of Level 1 SEPSS (monthly) and Level 2 SEPSS (quarterly) for 5 minutes or as specified for its class; annual test at full load for 60% of full duration of its class | NFPA 111-2010 8.4 | Monthly / Quarterly / Annually
Emergency power supply system (EPSS) inspected, including all associated components and batteries | NFPA 110-2010 8.3.1; 8.3.3; 8.3.4; 8.4.1 | Weekly
Emergency generators tested for 30 continuous minutes under load, plus cool-down | NFPA 99-2012 6.4.4.1 | Monthly
EP 28 completeness test - every record above must show: activity name; date; inventory of devices, equipment or other items; frequency; contact information for the person performing the activity; the NFPA standard; and the activity results. A vendor cover sheet that is not integrated into the test results may not be accepted. (NFPA 25-2011 4.3, 4.4; NFPA 72-2010 14.2.1-14.2.4)

## 3 Deficiency to Closure
Deficiency to Closure Tracker
A deficiency is not closed when it is repaired. It is closed when the repair is verified and the evidence is filed. Never make the surveyor connect these dots.
ID | Building / Location | Source | Date found | Description | Risk | LSRA done? | ILSM required? | ILSM in place | Responsible party | Work order # | Target date | Completed | Verified by / evidence
EX-1 | Tower A, 3rd floor, Rm 314 corridor | Annual fire door inspection | 2026-08-12 | Fire door will not latch under self-closing force | High | Yes | Yes | Door held open under staff watch; daily check logged | Facilities - D. Ruiz | WO-44182 | 2026-09-15 |  | Pending reinspection

## 4 Fire Drill Matrix
Fire Drill Matrix - Five Quarters
TJC's document tool asks for five quarters of fire drill data. Health care occupancies drill once per shift per quarter. Vary the time of day quarter to quarter, and transmit the alarm signal.
Quarter | Building | Shift | Date | Time started | Alarm signal transmitted? | Staff participated | Scenario / location | Critique completed | Corrective action | Binder tab
Q1 (oldest) |  | 1st (day)
Q1 (oldest) |  | 2nd (evening)
Q1 (oldest) |  | 3rd (night)
Q2 |  | 1st (day)
Q2 |  | 2nd (evening)
Q2 |  | 3rd (night)
Q3 |  | 1st (day)
Q3 |  | 2nd (evening)
Q3 |  | 3rd (night)
Q4 |  | 1st (day)
Q4 |  | 2nd (evening)
Q4 |  | 3rd (night)
Q5 (current) |  | 1st (day)
Q5 (current) |  | 2nd (evening)
Q5 (current) |  | 3rd (night)
Ambulatory health care occupancies drill quarterly. Business occupancies drill every 12 months from the date of the last drill. Drills are held at unexpected times and under varying conditions, and the time of day is varied quarter to quarter through four consecutive quarters.

## 5 Survey Day Log
Survey Day Request Log
Fill this in live. Anything over 60 seconds is next year's homework. Document review is capped at 4 hours and usually runs 90-120 minutes - the queue is the constraint.
Time | What the surveyor asked for | Where it came from (binder / tab / system) | Who produced it | Seconds to produce | Accepted? | Follow-up needed

## 6 Binder Spines
Binder Spines & Covers
Print at Actual Size (not Fit to Page), cut on the lines, slide into the spine pocket. 3-inch binder spine = 2.5in wide.
0 | SURVEY COMMAND | Index ¦ Drawings ¦ SOC ¦ AHJ ¦ Waivers
1 | FIRE ALARM | NFPA 72 ¦ Annual ¦ Devices ¦ Monitoring
2 | SUPPRESSION | NFPA 25 ¦ Sprinkler ¦ Pump ¦ Kitchen
3 | BARRIERS & DOORS | NFPA 80 ¦ Doors ¦ Dampers ¦ Penetrations
4 | EMERGENCY POWER | NFPA 110 ¦ Generator ¦ EPSS ¦ Lighting
5 | MEDICAL GAS & UTILITIES | NFPA 99 ¦ Med gas ¦ Utilities ¦ Water
6 | FIRE DRILLS | Five quarters ¦ Every shift ¦ Critiques
7 | LSRA / ILSM | Risk ¦ Interim measures ¦ Fire watch
8 | DEFICIENCIES | Found ¦ Assessed ¦ Corrected ¦ Verified