## Tool
Determining Risk Tolerance
Risk Tolerance |  | Severity of Occurrence
|  | Category 1 Life safety deficiency likely to cause major injury or death (1) | Category 2 Life safety deficiency likely to cause minor injury (2) | Category 3 Life safety deficiency not likely to cause injury (3) | Category 4 Life safety deficiency likely has minimal impact to safety (4)
Impact of Deficiency | Facility Wide Impacts the entire facility (1) | High Needs Specific Remediation Actions | High Needs Specific Remediation Actions | Medium Needs Remedial Action | Low Risk Acceptable Remedial Action Discretionary
| Multiple Units/Floors Impacts multiple smoke compartments (2) | High Needs Specific Remediation Actions | High Needs Specific Remediation Actions | Medium Needs Remedial Action | Low Risk Acceptable Remedial Action Discretionary
| Local/Single Unit Impacts a single smoke compartment or area (3) | High Needs Specific Remediation Actions | Medium Needs Remedial Action | Medium Needs Remedial Action | Low Risk Acceptable Remedial Action Discretionary
| Short Duration Correction can be performed during shift Identified (4) | No ILSM Required -
Date: Location Address: Action(s) Taken: Creation of Corrective Action Plan, ILSM created, notified engineering. Person Completing Life Safety Risk Matrix: ILSM Required? YES
Deficiency Examples: | [5 empty] | Impact | Severity | Risk Level
Fire/Smoke Doors
Door latching problem not immediately repairable. | [5 empty] | 3 | 3 | Medium
Hardware not fire rated | [5 empty] | 3 | 4 | Low
Damaged Hardware | [5 empty] | 3 | 2 | High
Excessive undercut | [5 empty] | 3 | 4 | Low
Fire Alarm
Pull station mounted too high | [5 empty] | 3 | 4 | Low
Smoke detector missing above fire alarm panel | [5 empty] | 3 | 2 | Medium
Damaged devices/appliances | [5 empty] | 2 | 2 | High
Taking a detection/suppression system out of service for repair/modification <4 hours. | [5 empty] | 1 | 3 | Medium
Taking a detection/suppression system out of service for repair/modification >4 hours. | [5 empty] | 1 | 2 | High
Sprinkler System
Missing escutcheon plate | [5 empty] | 4 | 4 | No ILSM
Storage within 18" of sprinkler head deflector | [5 empty] | 4 | 4 | No ILSM
Dusty sprinkler heads. | [5 empty] | 3 | 4 | Low
Items attached or supported by sprinkler system | [5 empty] | 1 | 3 | Medium
Fire/Smoke Barriers
Improperly protected vertical opening(s). | [5 empty] | 2 | 1 | High
Corridor walls do no not extend to the structure. | [5 empty] | 2 | 1 | High
Unprotected penetrations in fire or smoke barriers. | [5 empty] | 2 | 3 | Medium
Hazardous areas not properly protected. | [5 empty] | 3 | 2 | Medium
Means of Egress
Obstruction to minimum egress width. | [5 empty] | 4 | 4 | No ILSM
Storage within exit enclosure. | [5 empty] | 2 | 4 | Low
Fire exit stairs discharge improperly. | [5 empty] | 2 | 2 | High
Excessive travel distance to an approved exit. | [5 empty] | 3 | 1 | High
Blocking of an exit due to construction activities. | [5 empty] | 3 | 2 | Medium